## PFC
Power Factor Correction using Static Capacitor | [6 empty] | short circuit impedance voltage of the transformer %
Calculation Formulas as follows | [6 empty] | >>>>> | Oil type transformer |  | . | Dry type transformer
Q1= (I Losses)+(Cu losses). |  |  |  |  | **I losses =2% x(Str) |  |  | Rating (KVA) | Usc (%) |  | Rating (KVA) | Usc (%)
Q2 =PkW x (Tanφ1-Tanφ2). |  |  |  |  | **CU losses =USC% x(Str) |  | . | 50 | 4 | . | 100 | 6
Q = Q1 + Q2. | [6 empty] | . | 63 | 4 | . | 160 | 6
Q1 = Reactive power to be compensated at the terminals of a transformer due to no load & load losses. | [6 empty] | . | 100 | 4 | . | 200 | 6
Q2 = Reactive power to be compensated due to total reactive components of lighting, power & Mechanical loads. | [6 empty] | . | 160 | 4 | . | 250 | 6
Q = Overall reactive power to be compensated to achieve target power factor. | [6 empty] | . | 200 | 4 | . | 315 | 6
I losses = Transformer no load losses = Iron core losses. | [6 empty] | . | 300 | 4 | . | 400 | 6
CU losses = Transformer load losses = Copper losses. | [6 empty] | >>>>> | 500 | 4 | . | 500 | 6
Str = Transformer rating (KVA). | [6 empty] | . | 800 | 5 | . | 630 | 6
P = Maximum demand load on the Main distribution board (kW). | [6 empty] | . | 1000 | 5 | . | 800 | 6.5
φ1 = Inverse cosine of power factor before compensation. | [6 empty] | . | 1500 | 5 | . | 1000 | 6.5
φ2 = Inverse cosine of target power factor. | [6 empty] | . | 2000 | 7 | . | 1250 | 6.5
Usc% = Short circuit percentage impedance voltage of the transformer | [6 empty] | . | 2500 | 7 | . | 1600 | 7
Power Factor Values assumptions before compensation. | [6 empty] | . | 3000 | 7.4 | . | 2000 | 7
For Lighting outlets = 0.96 | [9 empty] | . | 2500 | 7
For power outlets & receptacles = 0.8 | [9 empty] | . | 3150 | 7
For Motors = 0.8
Power Factor Correction calculations for power system
Trans. rating | = | 500 | kVA |  | Fill in Cells with this color |  | The permitted range of applied voltage at fundamental frequency, plus harmonic
Trans. Type | = | oil |  |  |  |  | components, together with manufacturing tolerances of actual capacitance (for a
Usc% | = | 0.04 |  |  |  |  | declared nominal value) can result in a 50% increase above the calculated value of
PkVA | = | 392 | kVA |  |  |  | current. Approximately 30% of this increase is due to the voltage increases, while a
Cosφ1 | = | 0.82 |  |  | **P.F before compensation |  | further 15% is due to the range of manufacturing tolerances, so that
PkW | = | 321.44 | kW |  |  |  | 1.3 x 1.15 = 1.5
Cosφ2 | = | 0.92 |  |  | **Target Power factor
φ1 | = | 34.9152
φ2 | = | 23.0739 |  |  |  |  | The capacitors will draws a leading current and partly or completely neutralize the lagging reactive
Tanφ1 | = | 0.698 |  |  |  |  | component of the load current. This This raises the power factor of the load.
Tanφ2 | = | 0.426
Q1= (I Losses)+(Cu losses). | [6 empty] | Qc = Sqrt(3) (I)(V) SINφ
Q1 | = | 30 | kVAr
Q2 =PkW x (Tanφ1-Tanφ2).
Q2 | = | 87.4336 | kVAr
Q = Q1 + Q2.
Q | = | 117.4336 | kVAr
The required capacitor bank (QC) to compensate (Q) |  |  |  | = | 120 | kVAr
Qc = Sqrt(3) (I)(V) Sinφ |  |  | Sinφ = 1
The nominal current (In) of a 3-phase capacitor bank = |  |  |  |  | QC / (SQRT(3)X (V))
In | = | 173.2051 | Ampere | @ | System Voltage (kV) = | 0.4
1.5 x In | = | 259.8076 | Ampere | 50% increase in current due to harmonics and manufacturer tolerances
Circuit Breaker Rating Protecting the capacitor bank |  |  |  | = | 320 | Ampere
Note on C22: Dry type Oil type
Note on A1: Mahmoud Salama